###### RH-xU-D-T 
Duct humidity and temperature transmitter

Features

- Humidity and temperature measurement for air ducts

- Simple and secure installation

- 4…20mA measuring signals

- Compact size and modern design

Applications

- On return air ducts to measure return air humidity and temperature

- On supply air ducts to measure supply air humidity and temperature

- On fresh air ducts to measure outdoor ari humidity and temperature.

Humidity Transmitter

The transmitter measures the humidity by the honeywell humidity sensor HIH-5030. The transmitter analog output may be 4-20mA. And the transmitter include a noise filter. the power supply is large range VDC18V----VDC30V.The humidity transmitter measurement range is 5%-95%.

linearity Signal output:

HIMAX

HIMin

Y [%]

100%

0%

H[0-100]

## Ordering

Ordering number:RH-5U-D

-5  indicates the humidity transmitter accuracy is 5%; -3 indicates 3%, -2 indicates 2%.

-U indicates the humidity transmitter signal out is 4-20mA.

-T  indicates the temperature range is 0 – 50℃; -T3 indicates -20 – 60℃.

For example:RH-5U-D-T

The duct humidity and temperature transmitter signal out is 4-20mA

## Installation

Duct probes should be installed directly on the duct, in an area where the air stream is well mixed:

- Locate a supply air sensor two or three meters down stream from the nearest fan and coil.

- Mount the return air sensor close to the air inlet but downstream from a return fan if one is present.

- To install the sensor, assemble base plate and probe, then drill a 12 mm hole and two 3 mm holes on a diameter of 25 mm in the duct.

- Use two self-tapping sheet metal screws to tighten the mounting circuit in the cover.

- Connect the wires according to the wiring diagram to the measuring circuit in the cover:

  - Only the humidity transmitter signal out  need three terminal connections,DC24V,Ground and humidity signal out.

  - If humidity and temperature transmitter signal out need for terminal connections,DC24V,Ground,humidity signal out and temperature signal out.

  - The connection signal cable should be shield wires.

- Assemble the cover with the mounting plate.

- Insert the assembled probe through the center opening of the mounting plate into the air stream.

- Tighten the horizontal screw on the mounting plate to fix the probe to the duct.

## Technical Specification

| Power supply | Option voltage | DC 24V or AC 24V |
| --- | --- | --- |
|  | Power Consumption | Max 2 VA |
| Signal out | signal | 4-20mA |
|  | accuracy | Humidity 5% ; temperature 0.5℃ |
|  | Humidity range | 0%-100% |
|  | temperature range | 0 - 50°C |
| Connection | Connection Terminals | 2.5 mm2 |
| Environment | Operation Climatic Conditions Temperature Humidity | To IEC 721-3-3 class 3 K5 -40…70°C <95% RH. |
|  | Transport & Storage Climatic Conditions Temperature Humidity Mechanical Conditions | To IEC 721-3-2 and IEC 721-3-1 class 3 K3 and class 1 K3 -40…80°C <95% RH. class 2M2 |
| Standards | conform according to EMC Standard 89/336/EEC EMEI Standard 73/23/EEC | EN 61 000-6-1/ EN 61 000-6-3 |
|  | Automatic electrical controls for household and similar use Special requirement on temperature dependent controls | EN 60 730 –1 EN 60 730 – 2 - 9 |
|  | Pollution Class | Normal acc. To EN 60 730,RoHS compliant |
|  | Degree of Protection | IP56 to EN 60 529 |
| Housing Materials | Cover & Mounting Plate | Fire proof ABS plastic |
| General | Dimensions [mm] | Cover: 42 x 112 x 88 (H x W x D) probe: ø 14 x 200 (Diameter x L) |
|  | Weight (including package) | 135g |

## Wire diagram

Terminal connections

- power supply DC24V or AC 24V

- power supply ground or signal ground

- Humidity signal output 4~20mA

- Temperature singal output 4~20mA

1

2

3

4

ADC24

GND

RH

T

81

28

15

61

12

14

dimension [mm]

81

81