###### MG-BACIP
BACnet  to Modbus Gate

## Features and Highlights

- Interoperable

Modbus -compliant controller supports BACnet data form slave nodes on an BACIP network.

- Versatile

Supports 100 analog and  100 binary values integrate BACnet device data with a Modbus system.

- Reliable

Extensive onboard filtering, with all program data backed up in nonvolatile flash memory.

- Ecomomical

Simple, low cost solution for field-level integration of BACnet device.

## Applications and functions

- The Hysine MG-BACIP is a field-level gateway that resides on a Modbus network and connects to BACIP over RJ-45,translating BACnet data to Modbus AVs and BVs. The MG-BACIP appears to the Modbus system in the same manner as a Modbus MCU,with a single Modbus device instance.

- The MG-BACIP offers a point capacity of 100 MOBUS AI/AO/AV and 100 BI/BO/BV an ideal point count for most BACnet applications. A single MG-MSTP supports up to 10 BACnet devices on a multi-drop BACnet MS/TP network.

- The MG-BACIP is the next-generation BACnet to Modbus gate from Hysine. Each MG-BACIP supports field controllers on one BACIP LANs and one Modbus LANs. BACIP is a simple RJ-45 port with a configurable speed to 76.8 Kbps. Modbus LANs is a simple twisted-pair bus with a configurable speed to 9.6 Kbps.

- CMOS circuitry,a four layer circuit board with separate ground plane, and extensive hardware software,and power-supply filtering ensure reliable and stable operatio. The CMOS processor uses an internal watchdog,and power supply voltage is monitored to provide automatic shutdown and data backup.

## Ordering information

Item number                                             Description                                              .

MG-BACIP                                                 BACnet to Modbus Gate

Technical Data

- Power   24 VAC @ 10VA. Utilizes a half-wave rectifier, which allows a single transformer to power Multiple MGs. One leg of 24VAC connects to earth (panel) ground.

- Battery   Replaceable 3.0V lithium battery provides up to 1.5 years(cumulative) real-time clock(without external power supply). Standby battery life is 10 years. Coin-cell type BR1225 or equivalent.

- Processor & memory    AVR processor with onboard flash memory and RAM.

- BACIP   Removable, header-style screw terminal for 1 BACIP(RJ-45 port) LANs,each individually configurable from 76.8 Kbps.

- Modbus Communications  Multi-drop EIA-485 (twisted pair) to up to 10 Modbus device. Network options configurable for ASCⅡ/RTU, 4800 and 9600 baud, even/odd/no parity, and stop bit options for compatibility with various modbus implementations.

- Dimensions    (112mm)H × (140mm)W × (38mm)D

- Environmental   0-55℃.0-95%RH,non-condensing.

- Software   Support for 100 BACnet AVs and 100 BVs, each mapped to a Modbus data point through a string written to the description property of the AV or BV object.

- Ratings   EMC  GB/T 17626

## Dimension[mm]