###### TS-XX-D-YY
Duct Temperature Sensor

## Features

- Thermistor，PT or NI sensing elements to fit your system

- Simple and secure installation

- Wide range of temperature probes

- Compact size and modern design

## Applications

- On return air ducts to measure heating/cooling return air

- On supply air ducts to measure heating/cooling supply air

- In heat exchangers and air handling units to control heating/cooling coils for temperature and humidity control

- As frost protection sensor

## Temperature Sensor

The sensor measures the temperature by use of a NTC, PT or NI sensing element. The sensing element is either a glass packed thermistor with a negative temperature coefficient or a platinum film sensor or a thin nickel layer on a ceramic substrate. Its resistance changes according to the temperature. The change follows a specified curve. Below is a list of available sensor elements, curves and accuracies:

| Item name | Sensing element | Curve | Compatible with |
| --- | --- | --- | --- |
| N18 | Thermistor 1.8k at 25 °C | Curve 5 | TAC, CSI |
| N3 | Thermistor 3k at 25 °C | Curve 6 | Alerton |
| N10 | Thermistor 10k at 25 °C | Curve 24 | Hysine, Alerton,ALC, Delta,Trane, CSI |
| N11 | Thermistor 10k at 25 °C | Curve 7 | Andover, Invensys, Carrier, KMC |
| N20 | Thermistor 20k at 25 °C | Curve 20 | Honeywell |
| N100 | Thermistor 100k at 25 °C | Curve 9 | Siemens SBT |
| Tp1 | PT100 | 0.3851ohm/K | Honeywell |
| Tp2 | PT1000 | 3.851ohm/K | Johnson Control |
| NI1 | NI1000 | 5000ppm/k | Siemens SBT |

## Ordering

Ordering number:TS-XX-D-YY

XX indicates the sensor element optional，see table above.

YY indicates the probe length. Standard probe length is 20 cm.

For example:TS-N10-D-20

-N10 indicates the sensor element is Thermistor 10k .

-20     indicates the probe length is 20 cm.

## Installation

Duct probes should be installed directly on the duct, in an area where the air stream is well mixed:

- Locate a supply air sensor two or three meters down stream from the nearest fan and coil.

- Mount the return air sensor close to the air inlet but downstream from a return fan if one is present.

- To install the sensor, assemble base plate and probe, then drill a 8 mm hole and two 3 mm holes on a diameter of 25 mm in the duct.

- Use two self-tapping sheet metal screws to tighten the mounting circuit in the cover.

- Connect the wires according to the wiring diagram to the measuring circuit in the cover:

  - The Thermistors require two conductors; normally 18ga unshielded twisted pair.

  - The PT100, PT1000 and NI1000 sensors come with each two terminal connectors in order to connect up to four conductors for compensating conductor resistance.

- Assemble the cover with the mounting plate.

- Insert the assembled probe through the center opening of the mounting plate into the air stream.

- Tighten the horizontal screw on the mounting plate to fix the probe to the duct.

## Technical Specification

| Sensing Probe | Thermistor: Range Accuracy | NTC -30----110°C ±0.5k |
| --- | --- | --- |
|  | Platinum-Film: Range Accuracy | PT, 0.3851ohm/k -30----70°C ±0.3k |
|  | Nickel Thin Layer Range Accuracy | NI, 5000 ppm/k -30----70°C ±1k |
| Connection | Connection Terminals | 2.5 mm2 |
| Environment | Operation Climatic Conditions Temperature Humidity | To IEC 721-3-3 class 3 K5 -40…70°C <95% r.h. |
|  | Transport & Storage Climatic Conditions Temperature Humidity Mechanical Conditions | To IEC 721-3-2 and IEC 721-3-1 class 3 K3 and class 1 K3 -40…80°C <95% r.h. class 2M2 |
| Standards | conform according to EMC Standard 89/336/EEC EMEI Standard 73/23/EEC | EN 61 000-6-1/ EN 61 000-6-3 |
|  | Automatic electrical controls for household and similar use Special requirement on temperature dependent controls | EN 60 730 –1 EN 60 730 – 2 - 9 |
|  | Pollution Class | Normal acc. To EN 60 730,RoHS compliant |
|  | Degree of Protection | IP56 to EN 60 529 |
|  | Safety Class | III (IEC 60536) |
| Housing Materials | Cover & Mounting Plate Probe | Fire proof ABS plastic Stainless Steel |
| General | Dimensions [mm] | Cover: 42 x 112 x 88 (H x W x D) Probe: ø 6 x 200 (Diameter x L) |
|  | Weight (including package) | 135g |

## Wiring Diagram

1

2

RT1

RT2

Dimension [mm]